## dtsu666_modbus
No. | Signal Name | Read/Write | Data Type | Unit | Gain | Register Address | Quantity | Description
1 | Meter status | RO | UINT1 6 | N/A | 1 | 37100 | 1 | 0: offline 1: normal
2 | Grid voltage (A phase) | RO | INT32 | V | 10 | 37101 | 2
3 | B phase voltage | RO | INT32 | V | 10 | 37103 | 2
4 | C phase voltage | RO | INT32 | V | 10 | 37105 | 2
5 | Grid current(A phase) | RO | INT32 | A | 100 | 37107 | 2
6 | B phase current | RO | INT32 | A | 100 | 37109 | 2
7 | C phase current | RO | INT32 | A | 100 | 37111 | 2
8 | Active power | RO | INT32 | W | 1 | 37113 | 2 | >0: feed-in to the power grid. <0: supply from the power grid.
9 | Reactive power | RO | INT32 | Var | 1 | 37115 | 2
10 | Power factor | RO | INT16 | NA | 1000 | 37117 | 1
11 | Grid frequency | RO | INT16 | Hz | 100 | 37118 | 1
12 | Positive active electricity | RO | INT32 | kWh | 100 | 37119 | 2 | Electricity fed by the inverter to the power grid.
13 | Reverse active power | RO | INT32 | kWh | 100 | 37121 | 2 | Power supplied to a distributed system from the power grid.
14 | Accumulated reactive power | RO | INT32 | kVar h | 100 | 37123 | 2
15 | Meter type | RO | UINT1 6 | N/A | 1 | 37125 | 1 | 0: single-phase. 1: three-phase.
16 | A-B line voltage | RO | INT32 | V | 10 | 37126 | 2
17 | B-C line voltage | RO | INT32 | V | 10 | 37128 | 2
18 | CA line voltage | RO | INT32 | V | 10 | 37130 | 2
19 | A phase active power | RO | INT32 | W | 1 | 37132 | 2 | > 0: feed-in to the power grid. <0: supply from the power grid
20 | B phase active power | RO | INT32 | W | 1 | 37134 | 2 | > 0: feed-in to the power grid. <0: supply from the power grid
21 | C phase active power | RO | INT32 | W | 1 | 37136 | 2 | > 0: feed-in to the power grid. <0: supply from the power grid
22 | Meter model detection result | RO | UINT1 6 | N/A | 1 | 37138 | 1 | 0: being identified 1: The selected model is the same as the actual model of the connected meter. 2: The selected model is different from the actual model of the connected meter.

## luna2000_modbus
No. | Signal Name | Read/Write | Data Type | Unit | Gain | Register Address | Quantity | Description | HUAWEI LUNA2000 | LG RESU
1 | [Energy storage unit 1] [1] Running status | RO | UIN T16 | N/A | 1 | 37000 | 1 | 0: offline 1: standby 2: running 3: fault 4: sleep mode | √ | （√）[2]
2 | [Energy storage unit 1] Charge and discharge power | RO | INT3 2 | W | 1 | 37001 | 2 | > 0: charging < 0: discharging | √ | （√）
3 | [Energy storage unit 1] Bus voltage | RO | UIN T16 | V | 10 | 37003 | 1 | Energy storage module output voltage | √ | （√）
4 | [Energy storage unit 1] Battery SOC | RO | UIN T16 | % | 10 | 37004 | 1 | Battery's state of capacity | √ | （√）
5 | [Energy storage unit 1] Working mode | RO | UIN T16 | N/A | 1 | 37006 | 1 | 0: none 1: Forcible charge/discharge 2: Time of Use (LG) 3: Fixed charge/discharge 4: Maximise self-consumption 5: Fully fed to grid 6: Time of Use (LUNA2000) 7: Remote scheduling - maximum self-use 8: Remote scheduling - full Internet access 9: Remote scheduling - TOU 10: AI energy management and scheduling | √ | √
6 | [Energy storage unit 1] Rated charge power | RO | UIN T32 | W | 1 | 37007 | 2 | - | √ | √
7 | [Energy storage unit 1] Rated discharge power | RO | UIN T32 | W | 1 | 37009 | 2 | - | √ | √
8 | [Energy storage unit 1] Fault ID | RO | UIN T16 | N/A | 1 | 37014 | 1 | - | √ | √
9 | [Energy storage unit 1] Current-day charge capacity | RO | UIN T32 | kWh | 100 | 37015 | 2 | - | √ | （√）
10 | [Energy storage unit 1] Current-day discharge capacity | RO | UIN T32 | kWh | 100 | 37017 | 2 | - | √ | （√）
11 | [Energy storage unit 1] Bus current | RO | INT1 6 | A | 10 | 37021 | 1 | Energy storage module output current | √ | √
12 | [Energy storage unit 1] batter y temperature | RO | INT1 6 | ℃ | 10 | 37022 | 1 | - | √ | √
13 | [Energy storage unit 1] Remaining charge/discharge time | RO | UIN T16 | mins | 1 | 37025 | 1 | [0,1440] | √
14 | [Energy storage unit 1] DCDC version | RO | STRI | N/A | 1 | 37026 | 10 | eg. 7kW- V1.3 |  | √
NG
15 | [Energy storage unit 1] BMS version | RO | STRI | N/A | 1 | 37036 | 10 | eg. 1 2 3 4 |  | √
NG
16 | [Energy storage] Maximum charge power | RO | UIN T32 | W | 1 | 37046 | 2 | The value is the smaller value of the sum of the maximum charge and discharge capability of the solar inverter and the charge and discharge capability of the connected Energy storage unit (ESU). | √ | √
17 | [Energy storage] Maximum discharge power | RO | UIN T32 | W | 1 | 37048 | 2 | The value is the smaller value of the sum of the maximum charge and discharge capability of the solar inverter and the charge and discharge capability of the connected ESU. | √ | √
18 | [Energy storage unit 1] SN | RO | STRI | N/A | 1 | 37052 | 10 | - | √ | √
NG
19 | [Energy storage unit 1] Total charge | RO | UIN T32 | kWh | 100 | 37066 | 2 | - | √ | √
20 | [Energy storage unit 1] Total discharge | RO | UIN T32 | kWh | 100 | 37068 | 2 | - | √ | √
21 | [Energy storage unit 2] SN | RO | BYTE S | N/A | 1 | 37700 | 10 | - | √
22 | [Energy storage unit 2] Battery SOC | RO | UIN T16 | % | 10 | 37738 | 1 | Battery's state of capacity | √
23 | [Energy storage unit 2] Running status | RO | UIN T16 | N/A | 1 | 37741 | 1 | 0: offline 1: standby 2: running 3: fault 4: sleep mode | √
24 | [Energy storage unit 2] Charge and discharge power | RO | INT3 2 | W | 1 | 37743 | 2 | > 0: charging < 0: discharging | √
25 | [Energy storage unit 2] Current-day charge capacity | RO | UIN T32 | kWh | 100 | 37746 | 2 | - | √
26 | [Energy storage unit 2] Current-day discharge capacity | RO | UIN T32 | kWh | 100 | 37748 | 2 | - | √
27 | [Energy storage unit 2] Bus voltage | RO | UIN T16 | V | 10 | 37750 | 1 | - | √
28 | [Energy storage unit 2] Bus current | RO | INT1 6 | A | 10 | 37751 | 1 | - | √
29 | [Energy storage unit 2] Battery temperature | RO | INT1 6 | ℃ | 10 | 37752 | 1 |  | √
30 | [Energy storage unit 2] Total charge | RO | UIN T32 | kWh | 100 | 37753 | 2 | - | √
31 | [Energy storage unit 2] Total discharge | RO | UIN T32 | kWh | 100 | 37755 | 2 | - | √
32 | [Energy storage] Rate d capacity | RO | UIN T32 | Wh | 1 | 37758 | 2 |  | √
33 | [Energy storage] SOC | RO | UIN T16 | % | 10 | 37760 | 1 | [0.0,100.0] | √
34 | [Energy storage] Run ning status | RO | UIN T16 | N/A | 1 | 37762 | 1 | 0: offline 1: standby 2: running 3: fault 4: sleep mode | √
35 | [Energy storage] Bus voltage | RO | UIN T16 | V | 10 | 37763 | 1 | - | √
36 | [Energy storage] Bus current | RO | INT1 6 | A | 10 | 37764 | 1 | - | √
37 | [Energy storage] Charge/Discharge power | RO | INT3 2 | W | 1 | 37765 | 2 | - | √
38 | [Energy storage] Total charge | RO | UIN T32 | kWh | 100 | 37780 | 2 | Lifecycle accumulation | √ | √
39 | [Energy storage] Total discharge | RO | UIN T32 | kWh | 100 | 37782 | 2 | Lifecycle accumulation | √ | √
40 | [Energy storage] Current-day charge capacity | RO | UIN T32 | kWh | 100 | 37784 | 2 | currentday accumulation | √ | √
41 | [Energy storage] Current-day discharge capacity | RO | UIN T32 | kWh | 100 | 37786 | 2 | currentday accumulation | √ | √
42 | [Energy storage unit 2] softwa re version | RO | STRI | N/A | 1 | 37799 | 15 | - | √
NG
43 | [Energy storage unit 1] softwa re version | RO | STRI | N/A | 1 | 37814 | 15 | - | √
NG
44 | [Energy storage unit 1] [Battery pack 1] SOH Calibration Status | RO | UIN T16 | N/A | N/A | 37920 | 1
45 | [Energy storage unit 1] [Battery pack 2] SOH Calibration Status | RO | UIN T16 | N/A | N/A | 37921 | 1
46 | [Energy storage unit 1] [Battery pack 3] SOH Calibration Status | RO | UIN T16 | N/A | N/A | 37922 | 1
47 | [Energy storage unit 2] [Battery pack 1] SOH Calibration Status | RO | UIN T16 | N/A | N/A | 37923 | 1
48 | [Energy storage unit 2] [Battery pack 2] SOH Calibration Status | RO | UIN T16 | N/A | N/A | 37924 | 1
49 | [Energy storage unit 2] [Battery pack 3] SOH Calibration Status | RO | UIN T16 | N/A | N/A | 37925 | 1
50 | SOH Calibration Status | RO | UIN T16 | N/A | 1 | 37926 | 1
51 | SOH Calibration Release the lower discharge limit of the SOC | RO | UIN T16 | N/A | 10 | 37927 | 1
52 | SOH Calibration Enable the backup power SOC. | RO | UIN T16 | N/A | 10 | 37928 | 1
53 | [Energy storage unit 1] [Battery pack 1] SN | RO | STRI | N/A | N/A | 38200 | 10 | - | √
NG
54 | [Energy storage unit 1] [Battery pack 1] Firmware version | RO | STRI | N/A | N/A | 38210 | 15 | - | √
NG
55 | [Energy storage unit 1] [Battery pack 1] Working status | RO | UIN T16 | N/A | N/A | 38228 | 1 | - | √
56 | [Energy storage unit 1] [Battery pack 1] SOC | RO | UIN T16 | % | 10 | 38229 | 1 | - | √
57 | [Energy storage unit 1] [Battery pack 1] Charge/Discharge power | RO | INT3 2 | kW | 1000 | 38233 | 2 | - | √
58 | [Energy storage unit 1] [Battery pack 1] Voltage | RO | UIN T16 | V | 10 | 38235 | 1 | - | √
59 | [Energy storage unit 1] [Battery pack 1] Current | RO | INT1 6 | A | 10 | 38236 | 1 | - | √
60 | [Energy storage unit 1] [Battery pack 1] Total charge | RO | UIN T32 | kWh | 100 | 38238 | 2 | - | √
61 | [Energy storage unit 1] [Battery pack 1] Total discharge | RO | UIN T32 | kWh | 100 | 38240 | 2 | - | √
62 | [Energy storage unit 1] [Battery pack 2] SN | RO | STRI | N/A | N/A | 38242 | 10 | - | √
NG
63 | [Energy storage unit 1] [Battery pack 2] Firmware version | RO | STRI | N/A | N/A | 38252 | 15 | - | √
NG
64 | [Energy storage unit 1] [Battery pack 2] Working status | RO | UIN T16 | N/A | N/A | 38270 | 1 | - | √
65 | [Energy storage unit 1] [Battery pack 2] SOC | RO | UIN T16 | % | 10 | 38271 | 1 | - | √
66 | [Energy storage unit 1] [Battery pack 2] Charge/Discharge power | RO | INT3 2 | kW | 1000 | 38275 | 2 | - | √
67 | [Energy storage unit 1] [Battery pack 2] Voltage | RO | UIN T16 | V | 10 | 38277 | 1 | - | √
68 | [Energy storage unit 1] [Battery pack 2] Current | RO | INT1 6 | A | 10 | 38278 | 1 | - | √
69 | [Energy storage unit 1] [Battery pack 2] Total charge | RO | UIN T32 | kWh | 100 | 38280 | 2 | - | √
70 | [Energy storage unit 1] [Battery pack 2] Total discharge | RO | UIN T32 | kWh | 100 | 38282 | 2 | - | √
71 | [Energy storage unit 1] [Battery pack 3] SN | RO | STRI | N/A | N/A | 38284 | 10 | - | √
NG
72 | [Energy storage unit 1] [Battery pack 3] Firmware version | RO | STRI | N/A | N/A | 38294 | 15 | - | √
NG
73 | [Energy storage unit 1] [Battery pack 3] Working status | RO | UIN T16 | N/A | N/A | 38312 | 1 | - | √
74 | [Energy storage unit 1] [Battery pack 3] SOC | RO | UIN T16 | % | 10 | 38313 | 1 | - | √
75 | [Energy storage unit 1] [Battery pack 3] Charge/Discharge power | RO | INT3 2 | kW | 1000 | 38317 | 2 | - | √
76 | [Energy storage unit 1] [Battery pack 3] Voltage | RO | UIN T16 | V | 10 | 38319 | 1 | - | √
77 | [Energy storage unit 1] [Battery pack 3] Current | RO | INT1 6 | A | 10 | 38320 | 1 | - | √
78 | [Energy storage unit 1] [Battery pack 3] Total charge | RO | UIN T32 | kWh | 100 | 38322 | 2 | - | √
79 | [Energy storage unit 1] [Battery pack 3] Total discharge | RO | UIN T32 | kWh | 100 | 38324 | 2 | - | √
80 | [Energy storage unit 2] [Battery pack 1] SN | RO | STRI | N/A | N/A | 38326 | 10 | - | √
NG
81 | [Energy storage unit 2] [Battery pack 1] Firmware version | RO | STRI | N/A | N/A | 38336 | 15 | - | √
NG
82 | [Energy storage unit 2] [Battery pack 1] Working status | RO | UIN T16 | N/A | N/A | 38354 | 1 | - | √
83 | [Energy storage unit 2] [Battery pack 1] SOC | RO | UIN T16 | % | 10 | 38355 | 1 | - | √
84 | [Energy storage unit 2] [Battery pack 1] Charge/Discharge power | RO | INT3 2 | kW | 1000 | 38359 | 2 | - | √
85 | [Energy storage unit 2] [Battery pack 1] Voltage | RO | UIN T16 | V | 10 | 38361 | 1 | - | √
86 | [Energy storage unit 2] [Battery pack 1] Current | RO | INT1 6 | A | 10 | 38362 | 1 | - | √
87 | [Energy storage unit 2] [Battery pack 1] Total charge | RO | UIN T32 | kWh | 100 | 38364 | 2 | - | √
88 | [Energy storage unit 2] [Battery pack 1] Total discharge | RO | UIN T32 | kWh | 100 | 38366 | 2 | - | √
89 | [Energy storage unit 2] [Battery pack 2] SN | RO | STRI | N/A | N/A | 38368 | 10 | - | √
NG
90 | [Energy storage unit 2] [Battery pack 2] Firmware version | RO | STRI | N/A | N/A | 38378 | 15 | - | √
NG
91 | [Energy storage unit 2] [Battery pack 2] Working status | RO | UIN T16 | N/A | N/A | 38396 | 1 | - | √
92 | [Energy storage unit 2] [Battery pack 2] SOC | RO | UIN T16 | % | 10 | 38397 | 1 | - | √
93 | [Energy storage unit 2] [Battery pack 2] Charge/Discharge power | RO | INT3 2 | kW | 1000 | 38401 | 2 | - | √
94 | [Energy storage unit 2] [Battery pack 2] Voltage | RO | UIN T16 | V | 10 | 38403 | 1 | - | √
95 | [Energy storage unit 2] [Battery pack 2] Current | RO | INT1 6 | A | 10 | 38404 | 1 | - | √
96 | [Energy storage unit 2] [Battery pack 2] Total charge | RO | UIN T32 | kWh | 100 | 38406 | 2 | - | √
97 | [Energy storage unit 2] [Battery pack 2] Total discharge | RO | UIN T32 | kWh | 100 | 38408 | 2 | - | √
98 | [Energy storage unit 2] [Battery pack 3] SN | RO | STRI | N/A | N/A | 38410 | 10 | - | √
NG
99 | [Energy storage unit 2] [Battery pack 3] Firmware version | RO | STRI | N/A | N/A | 38420 | 15 | - | √
NG
100 | [Energy storage unit 2] [Battery pack 3] Working status | RO | UIN T16 | N/A | N/A | 38438 | 1 | - | √
101 | [Energy storage unit 2] [Battery pack 3] SOC | RO | UIN T16 | % | 10 | 38439 | 1 | - | √
102 | [Energy storage unit 2] [Battery pack 3] Charge/Discharge power | RO | INT3 2 | kW | 1000 | 38443 | 2 | - | √
103 | [Energy storage unit 2] [Battery pack 3] Voltage | RO | UIN T16 | V | 10 | 38445 | 1 | - | √
104 | [Energy storage unit 2] [Battery pack 3] Current | RO | INT1 6 | A | 10 | 38446 | 1 | - | √
105 | [Energy storage unit 2] [Battery pack 3] Total charge | RO | UIN T32 | kWh | 100 | 38448 | 2 | - | √
106 | [Energy storage unit 2] [Battery pack 3] Total discharge | RO | UIN T32 | kWh | 100 | 38450 | 2 | - | √
107 | [Energy storage unit 1] [Battery pack 1] Maximum temperature | RO | INT1 6 | ℃ | 10 | 38452 | 1 | - | √
108 | [Energy storage unit 1] [Battery pack 1] Minimum temperature | RO | INT1 6 | ℃ | 10 | 38453 | 1 | - | √
109 | [Energy storage unit 1] [Battery pack 2] Maximum temperature | RO | INT1 6 | ℃ | 10 | 38454 | 1 | - | √
110 | [Energy storage unit 1] [Battery pack 2] Minimum temperature | RO | INT1 6 | ℃ | 10 | 38455 | 1 | - | √
111 | [Energy storage unit 1] [Battery pack 3] Maximum temperature | RO | INT1 6 | ℃ | 10 | 38456 | 1 | - | √
112 | [Energy storage unit 1] [Battery pack 3] Minimum temperature | RO | INT1 6 | ℃ | 10 | 38457 | 1 | - | √
113 | [Energy storage unit 2] [Battery pack 1] Maximum temperature | RO | INT1 6 | ℃ | 10 | 38458 | 1 | - | √
114 | [Energy storage unit 2] [Battery pack 1] Minimum temperature | RO | INT1 6 | ℃ | 10 | 38459 | 1 | - | √
115 | [Energy storage unit 2] [Battery pack 2] Maximum temperature | RO | INT1 6 | ℃ | 10 | 38460 | 1 | - | √
116 | [Energy storage unit 2] [Battery pack 2] Minimum temperature | RO | INT1 6 | ℃ | 10 | 38461 | 1 | - | √
117 | [Energy storage unit 2] [Battery pack 3] Maximum temperature | RO | INT1 6 | ℃ | 10 | 38462 | 1 | - | √
118 | [Energy storage unit 2] [Battery pack 3] Minimum temperature | RO | INT1 6 | ℃ | 10 | 38463 | 1 | - | √
119 | [Energy storage unit 1] Product mode | RW | UIN T16 | N/A | 1 | 47000 | 1 | 0: None 1: LG-RESU 2: HUAWEI LUNA2000 | √ | √
120 | [Energy storage] Time-of-use electricity price periods | RW | MUL | N/A | 1 | 47028 | 41 | For details, see 5.4. |  | √
TIDA
TA
121 | [Energy storage] Maximum charging power | RW | UIN T32 | W | 1 | 47075 | 2 | [0, Upper threshold] Default value: 3500; | √ | √
122 | [Energy storage] Maximum discharging power | RW | UIN T32 | W | 1 | 47077 | 2 | [0, Upper threshold] Default value: 3500; | √ | √
123 | [Energy storage] Charging cutoff capacity | RW | UIN T16 | % | 10 | 47081 | 1 | [90,100] Default value: 100 | √ | （√）
124 | [Energy storage] Discharge cutoff capacity | RW | UIN T16 | % | 10 | 47082 | 1 | [12,20] Default value: 15 | √ | （√）
125 | [Energy storage] Forced charging and discharging period | RW | UIN T16 | mins | 1 | 47083 | 1 | [0,1440] The value is not stored. | √
126 | [Energy storage] Forced charging and discharging power | RW | INT3 2 | W | 1 | 47084 | 2 | [–Maximum discharge power, Maximum charge power] Forced charge/discharge power ≤ rated charge/discharge power. Do not store.
127 | [Energy storage] Working mode settings | RW | UIN T16 | N/A | 1 | 47086 | 1 | 0: Adaptive (fixed charge/discharge/maximum self-consumption) 1: Fixed charge/discharge 2: Maximum self-consumption 3: Time of Use (LG) 4: Fully fed to grid 5: Time of Use (LUNA) | √ | （√）
128 | [Energy storage] Charge from grid Function | RW | UIN T16 | N/A | 1 | 47087 | 1 | 0: Disabled 1: Enabled | √ | （√）
129 | [Energy storage] Grid charge cutoff SOC | RW | UIN T16 | % | 10 | 47088 | 1 | [20,1 00] Default: 50 | √ | （√）
130 | [Energy storage unit 2] Product model | RW | UIN T16 | N/A | 1 | 47089 | 1 | 0: none 1: LG- RESU 2: HUA WEILUNA 2000 | √
131 | [Energy storage] Forcible charge/discharge | RW | UIN T16 | N/A | 1 | 47100 | 1 | 0: Stop 1: charge 2: discharge | √
132 | [Energy storage] Target SOC | RW | UIN T16 | % | 10 | 47101 | 1 | [0,100]
133 | [Energy storage] Backup power SOC | RW | UIN T16 | % | 10 | 47102 | 1 | Definition: Reserved energy storage capacity in backup mode Setting range: [0,100] Execution range — LG: [12,100], default value: 15; LUNA: [0,100], default value: 0 | √ | √
134 | [Energy storage] Product model | RW | UIN T16 | N/A | 1 | 47106 | 1 | 0: None 1: LG RESU 2: HUAWEI LUNA2000
135 | [Energy storage unit 1] No. | RW | UIN T16 | N/A | 1 | 47107 | 1 | [0,65534] Default: 0, which means no equipment. | √
136 | [Energy storage unit 2] No. | RW | UIN T16 | N/A | 1 | 47108 | 1 | [0,65534] Default: 0, which means no equipment. | √
137 | [Energy storage] Fixed charging and discharging periods | RW | MUL | N/A | 1 | 47200 | 41 | For details, see 5.4. |  | √
TIDA
TA
138 | [Energy storage] Power of charge from grid | RW | UIN T32 | kW | 1000 | 47242 | 2 | [0, maximum power of charge from grid] | √ | √
139 | [Energy storage] Maximum power of charge from grid | RW | UIN T32 | kW | 1000 | 47244 | 2 | Default:200 0 | √ | √
140 | [Energy storage] Forcible charge/discharge settin g mode | RW | UIN T16 | N/A | 1 | 47246 | 1 | 0： Duration | √
141 | [Energy storage] Forcible charge power | RW | UIN T32 | kW | 1000 | 47247 | 2 | [0,maximum charge power] | √ | √
142 | [Energy storage] Forcible discharge power | RW | UIN T32 | kW | 1000 | 47249 | 2 | [0,maximum discharge power] | √ | √
143 | [Energy storage] Forced charging power level | RW | UIN T32 | kW | 1000 | 47251 | 2 | [0,Rated capacity] | √
144 | [Energy storage] Forced discharge capacity | RW | UIN T32 | kW | 1000 | 47253 | 2 | [0,Rated capacity] | √
145 | [Energy storage] Tim e of Use charging and discharging periods | RW | Byte s | N/A | 1 | 47255 | 43 | For details, see 5.4. | √
146 | [Energy storage] Excess PV energy use in TOU | RW | UIN T16 | N/A | 1 | 47299 | 1 | 0: Fed to grid 1: Charge Note: Bound to the grid code. Japan: fed to grid; other countries: charge. | √
147 | Active power control mode | RW | UIN T16 | N/A | 1 | 47415 | 1 | 0: Unlimited (default) 1: DI active scheduling 5: Zero-power grid connection 6: Power-limited grid connection (kW) 7: Power-limited grid connection (%)
148 | Maximum Feed Grid Power (kW) | RW | INT3 2 | Kw | 1000 | 47416 | 2 | [-1000, Plant capacity] Default: 0
149 | Maximum Feed Grid Power (%) | RW | INT1 6 | % | 10 | 47418 | 1 | [0,100] Default: 0
150 | [Dongle] [Plant] maximum charge-from-grid power | RW | UIN T32 | Kw | 1000 | 47590 | 2 | [0,30] | √ | √
151 | [Backup] Switch to off-grid | RW | UIN T16 | N/A | 1 | 47604 | 1 | 0: Switch from grid-tied to off-grid | √ | √
152 | [Backup] Voltage in independent operation | RW | UIN T16 | V | 1 | 47605 | 1 | 0: 101V 1: 202V | √ | √
153 | [Energy storage unit 1] [Battery pack 1] No. | RW | UIN T16 | N/A | N/A | 47750 | 1 | [0,65534] Default: 0, which means no equipment. | √
154 | [Energy storage unit 1] [Battery pack 2] No. | RW | UIN T16 | N/A | N/A | 47751 | 1 | [0,65534] Default: 0, which means no equipment. | √
155 | [Energy storage unit 1] [Battery pack 3] No. | RW | UIN T16 | N/A | N/A | 47752 | 1 | [0,65534] Default: 0, which means no equipment. | √
156 | [Energy storage unit 2] [Battery pack 1] No. | RW | UIN T16 | N/A | N/A | 47753 | 1 | [0,65534] Default: 0, which means no equipment. | √
157 | [Energy storage unit 2] [Battery pack 2] No. | RW | UIN T16 | N/A | N/A | 47754 | 1 | [0,65534] Default: 0, which means no equipment. | √
158 | [Energy storage unit 2] [Battery pack 3] No. | RW | UIN T16 | N/A | N/A | 47755 | 1 | [0,65534] Default: 0, which means no equipment. | √

## sun2000_modbus
No. | Signal Name | Read/Write | Data Type | Unit | Gain | Register Address | Quantity | Description
10 | Maximum reactive power (Qmax, fed to the power grid) | RO | I32 | kVar | 1000 | 30079 | 2 | N/A
11 | Maximum reactive power (Qmax, absorbed from the power grid) | RO | I32 | kVar | 1000 | 30081 | 2 | N/A
12 | Offering name of southbound device 1 | RO | String | N/A | N/A | 30561 | 15 | N/A
13 | Offering name of southbound device 2 | RO | String | N/A | N/A | 30576 | 15 | N/A
14 | Offering name of southbound device 3 | RO | String | N/A | N/A | 30591 | 15 | N/A
15 | Hardware version | RO | String | N/A | 1 | 31000 | 15
16 | Monitoring board SN | RO | String | N/A | N/A | 31015 | 10 | N/A
17 | Monitoring software version | RO | String | N/A | N/A | 31025 | 15 | N/A
18 | Master DSP version | RO | String | N/A | N/A | 31040 | 15 | N/A
19 | CPLD version | RO | String | N/A | N/A | 31070 | 15 | N/A
20 | AFCI version | RO | String | N/A | N/A | 31085 | 15 | N/A
21 | DC-MBUS version | RO | String | N/A | N/A | 31115 | 15 | N/A
22 | REGKEY | RO | String | N/A | 1 | 31200 | 10
23 | [Remote communicati on] Singlemachine remote communicati on | RO | Bitfield1 | N/A | N/A | 32000 | 1 | Bit 0: standby Bit 1: gridconnected
|  |  | 6 |  |  |  |  | Bit 2: gridconnected
normally
Bit 3: grid connection with derating due to power rationing Bit 4: grid connection with derating due to internal causes of the solar inverter Bit 5: normal stop
Bit 6: stop due to faults Bit 7: stop due to power rationing Bit 8: shutdown Bit 9: spot check
Bit 10: Off-grid operation Bit 11:Hot
Standby
Operation
24 | [Remote communicati on] Running status (monitoring processing) | RO | Bitfield1 | N/A | N/A | 32002 | 1 | Bit 0: locking status (0: locked; 1: unlocked) Bit 1: PV connection status (0: disconnected; 1: connected) Bit 2: DSP data collection (0: no; 1: yes)
6
25 | [Remote communicati on] Running status (power processing) | RO | Bitfield3 | N/A | N/A | 32003 | 2 | Bit 0: off-grid (0: on-grid; 1: off-grid) Bit 1: off-grid switch (0: disable; 1: enable)
|  |  | 2 |  |  |  |  | Bit2: DC switch (0: OFF, 1: ON) Bit3: On-grid operation (0:
off-grid operation, 1: on-grid operation) Bit4: Off-grid operation (0: offline and not running; 1: offline and running) Bit5: Standby (0: nonstandby; 1: standby)
26 | Alarm 1 | RO | Bitfield1 | N/A | N/A | 32008 | 1 | For details, see
|  |  | 6 |  |  |  |  | 5.1 Alarm
Information.
27 | Alarm 2 | RO | Bitfield1 | N/A | N/A | 32009 | 1 | For details, see
|  |  | 6 |  |  |  |  | 5.1 Alarm
Information.
28 | Alarm 3 | RO | Bitfield1 | N/A | N/A | 32010 | 1 | For details, see
|  |  | 6 |  |  |  |  | 5.1 Alarm
Information.
29 | ESN | RO | UINT16 | N/A | N/A | 32015 | 1 | N/A
30 | PV1 voltage | RO | I16 | V | 10 | 32016 | 1 | A maximum of 24 PV strings are supported. The number of PV strings read by the host is defined by the Number of PV strings signal. The voltage and current register addresses for each PV string are as follows: PVn voltage: 32014 + 2n
31 | PV1 current | RO | I16 | A | 100 | 32017 | 1 | PVn current: 32015 + 2n
32 | PV2 voltage | RO | I16 | V | 10 | 32018 | 1 | n indicates the PV string number, which ranges from 1 to 24.
33 | PV2 current | RO | I16 | A | 100 | 32019 | 1
34 | PV3 voltage | RO | I16 | V | 10 | 32020 | 1
35 | PV3 current | RO | I16 | A | 100 | 32021 | 1
36 | PV4 voltage | RO | I16 | V | 10 | 32022 | 1
37 | PV4 current | RO | I16 | A | 100 | 32023 | 1
38 | Input power | RO | I32 | kW | 1000 | 32064 | 2 | N/A
39 | Power grid voltage/Line voltage between phases A and B | RO | U16 | V | 10 | 32066 | 1 | When the output mode is L/N, L1/L2/N, or L1/L2,
Power grid voltage is used.
40 | Line voltage between phases B and C | RO | U16 | V | 10 | 32067 | 1 | When the output mode is L/N, L1/L2/N, or L1/L2, the information is invalid.
41 | Line voltage between phases C and A | RO | U16 | V | 10 | 32068 | 1 | When the output mode is L/N, L1/L2/N, or L1/L2, the information is invalid.
42 | Phase A voltage | RO | U16 | V | 10 | 32069 | 1 | When the output mode is L/N, L1/L2/N, or L1/L2, the information is invalid.
43 | Phase B voltage | RO | U16 | V | 10 | 32070 | 1 | When the output mode is L/N, L1/L2/N, or L1/L2, the information is invalid.
44 | Phase C voltage | RO | U16 | V | 10 | 32071 | 1 | When the output mode is L/N, L1/L2/N, or L1/L2, the information is invalid.
45 | Power grid current/ Phase A current | RO | I32 | A | 1000 | 32072 | 2 | When the output mode is L/N, L1/L2/N, or L1/L2,
Power grid current is used.
46 | Phase B current | RO | I32 | A | 1000 | 32074 | 2 | When the output mode is L/N, L1/L2/N, or L1/L2, the information is invalid.
47 | Phase C current | RO | I32 | A | 1000 | 32076 | 2 | When the output mode is L/N, L1/L2/N, or L1/L2, the information is invalid.
48 | Peak active power of current day | RO | I32 | kW | 1000 | 32078 | 2 | N/A
49 | Active power | RO | I32 | kW | 1000 | 32080 | 2 | N/A
50 | Reactive power | RO | I32 | kVar | 1000 | 32082 | 2 | N/A
51 | Power factor | RO | I16 | N/A | 1000 | 32084 | 1 | N/A
52 | Grid frequency | RO | U16 | Hz | 100 | 32085 | 1 | N/A
53 | Efficiency | RO | U16 | % | 100 | 32086 | 1 | N/A
54 | Internal temperature | RO | I16 | °C | 10 | 32087 | 1 | N/A
55 | Insulation resistance | RO | U16 | MΩ | 1000 | 32088 | 1 | N/A
56 | Device status | RO | ENUM1 | N/A | N/A | 32089 | 1 | 0x0000
|  |  | 6 |  |  |  |  | Standby:
initialization
0x0001 Standby: insulation resistance detection
0x0002 Standby: sunlight detection
0x0003
Standby: grid detecting 0x0100 Starting
0x0200 On-grid (Off-grid mode: running) 0x0201 Grid connected: power limited (Off-grid mode: running: power limited) 0x0202 Grid connected: self derating
(Off-grid mode: running: selfderating) 0x0203 Off-grid operation 0x0300 OFF: unexpected shutdown 0x0301 OFF: instructed shutdown 0x0302 OFF:
OVGR
0x0303 OFF: communication interrupted
0x0304 OFF: power limited
0x0305 OFF: manual startup required
0x0307 Shutdown: rapid shutdown
0x030A
Shutdown: commanded
rapid shutdown
0x030B Shutdown: The backup power system is abnormal.
0x0401 Grid scheduling: cosφ-P curve
0x0402 Grid scheduling: Q-U curve 0x0403 Grid scheduling: PFU curve 0x0405 Grid scheduling: Q-P curve 0x0600
Inspecting ongoing 0X0700 AFCI check 0X0800 I-V curve scanning
0X0A00
Running: griddisconnected and charged
0X0A01
Standby: The backup power system is abnormal.
0xA000
Standby: no irradiation
57 | Fault code | RO | U16 | N/A | N/A | 32090 | 1 | N/A
58 | Startup time | RO | EPOCHT IME | s | 1 | 32091 | 2 | Epoch seconds, local time
59 | Shutdown time | RO | EPOCHT IME | s | 1 | 32093 | 2 | Epoch seconds, local time
60 | Accumulate d energy yield | RO | U32 | kWh | 100 | 32106 | 2 | N/A
61 | Daily energy yield | RO | U32 | kWh | 100 | 32114 | 2 | N/A
62 | [Management system] Management system status | RO | UINT16 | N/A | 1 | 35127 | 1
63 | [Smart I-V Curve Diagnosis] Authorization function | RO | DBitfield 32 | N/A | 1 | 35136 | 2 | Bit 0: Smart I-V Curve Diagnosis
64 | [Smart I-V Curve Diagnosis] License status | RO | ENUM1 | N/A | N/A | 35138 | 1 | 0: No license
|  |  | 6 |  |  |  |  | 1: Normal 2: In grace period 3: Revoked
4: SN not match
5: Expired
65 | [Smart I-V Curve Diagnosis] License expiration time | RO | EPOCHT IME | s | 1 | 35139 | 2 | N/A
66 | License loading time | RO | EPOCHT IME | s | 1 | 35141 | 2 | N/A
67 | License revocation time | RO | EPOCHT IME | s | 1 | 35143 | 2 | N/A
68 | License SN | RO | String | N/A | 1 | 35145 | 10
69 | Revocation code | RO | String | N/A | 1 | 35155 | 64
70 | [4G] Module status | RO | ENUM1 | N/A | N/A | 35249 | 1 | 0: Card not found 1: Card registration failed
|  |  | 6 |  |  |  |  | 2: No connection 3: Low signal strength 4: Medium signal strength
5: High signal strength 0x6: Connected
0x100: Card in position 0x101: PIN required 0x102: PUK required 0xFFFF: Module not found
71 | [4G] IP address | RO | UINT32 | N/A | 1 | 35250 | 2
72 | [4G] Subnet mask | RO | UINT32 | N/A | 1 | 35252 | 2
73 | [4G] IMEI | RO | String | N/A | 1 | 35254 | 10
74 | [4G] Signal strength | RO | UINT16 | N/A | 1 | 35264 | 1 | [0,5]
75 | [4G] Maximum number of PIN attempts | RO | UINT16 | N/A | 1 | 35265 | 1
76 | [4G] PIN verification status | RO | ENUM1 | N/A | N/A | 35266 | 1 | 0: Initial state 1: Verifying...
6
77 | Original model name | RO | MLD/ | N/A | 1 | 35268 | 15
Bytes
78 | [Active] Adjustment mode | RO | MLD/ | N/A | N/A | 35300 | 4 | 0: percentage
|  |  | Bytes |  |  |  |  | 1: fixed value
79 | [Reactive] Adjustment mode | RO | MLD/ | N/A | N/A | 35304 | 4 | 0: power factor
|  |  | Bytes |  |  |  |  | 1: absolute value 2: Q/S
3: Q-U characteristic curve
(command ID: 0)
4: cosφ-P/Pn characteristic curve
(command ID:
0) 5: PF-U characteristic curve
(command ID:
0) 6: Q-P characteristic curve
(command ID:
0)
80 | [System level] charge/discharge mode | RO | ENUM1 | N/A | N/A | 37006 | 1 | 0: N/A 1: Forced charge/ discharge 2: Time-of-use 3: Fixed charge and discharge
|  |  | 6 |  |  |  |  | 4: Max. selfconsumption
5: Fully fed to
grid
6: TOU 7: Remote scheduling– Max. selfconsumption
8: Remote scheduling–
Fully fed to grid
9: Remote
scheduling–
TOU
10: AI control
11: Remote scheduling–AI control
12: Three-party scheduling
81 | [Power meter collection] Active power* | RO | I32 | W | 1 | 37113 | 2 | > 0: feeding power to the power grid < 0: obtaining power from the power grid
82 | [Optimizer] Total number of optimizers* | RO | U16 | N/A | 1 | 37200 | 1 | N/A
83 | [Optimizer] Number of online optimizers* | RO | U16 | N/A | 1 | 37201 | 1 | N/A
84 | [Optimizer] Feature data* | RO | U16 | N/A | 1 | 37202 | 1 | N/A
85 | System time | RW | EPOCHT IME | s | 1 | 40000 | 2 | [2000-1-1
00:00:00,
2068-12-31 23:59:59] Epoch seconds, local time
86 | [Power grid scheduling] Q-U characteristic curve mode* | RW | ENUM1 | N/A | N/A | 40037 | 1 | 0: nonhysteresis 1: hysteresis
6
87 | [Power grid scheduling] Q-U dispatch trigger power (%)* | RW | I16 | % | 1 | 40038 | 1 | [-100, 100]
88 | [Power grid scheduling] Fixed active power derated | RW | U16 | kW | 10 | 40120 | 1 | Scope: [0, Pmax]
89 | power factor | RW | I16 | N/A | 1000 | 40122 | 1 | (–1, –0.8]U[0.8,
1]
90 | [Power grid scheduling] Reactive power compensation (Q/S) | RW | I16 | N/A | 1000 | 40123 | 1 | [–1, 1] The device converts the value to a fixed value of Q for reactive power control. S indicates Smax.
91 | [Power grid scheduling] Active power percentage derating (0.1%) | RW | I16 | % | 10 | 40125 | 1 | Scope: [0, 100] Interface for fine adjustment of active power
92 | [Power grid scheduling] Fixed active power derated (W) | RW | U32 | W | 1 | 40126 | 2 | Scope: [0, Pmax]
93 | [Power grid scheduling] Reactive power compensation at night (kVar) | RW | I32 | kVar | 1000 | 40129 | 2 | [–Qmax, Qmax]
94 | [Power grid scheduling] cosφ-P/Pn characteristic curve | RW | MLD/ | N/A | N/A | 40133 | 21 | For details, see 5.2 Power Grid Scheduling.
Bytes
95 | [Power grid scheduling] Q-U characteristic curve | RW | MLD/ | N/A | N/A | 40154 | 21 | For details, see 5.2 Power Grid Scheduling.
Bytes
96 | [Power grid scheduling] PF-U characteristic curve | RW | MLD/ | N/A | N/A | 40175 | 21 | For details, see 5.2 Power Grid Scheduling.
Bytes
97 | [Power grid scheduling] Reactive power adjustment time | RW | U16 | s | 1 | 40196 | 1 | [1, 1000]. The default value is 10.
98 | [Power grid scheduling] Q-U power percentage to exit scheduling* | RW | I16 | % | 1 | 40198 | 1 | [0, 100]
99 | Startup | WO | ENUM1 | N/A | N/A | 40200 | 1 | 0: startup
6
100 | Shutdown | WO | ENUM1 | N/A | N/A | 40201 | 1 | 0: shutdown
6
101 | Grid code | RW | U16 | NA | NA | 42000 | 1 | For details, see 5.3 Grid Codes.
102 | [Power grid scheduling] Reactive power change gradient | RW | U32 | %/s | 1000 | 42015 | 2 | [0.1, 5000]
103 | [Power grid scheduling] Active power change gradient | RW | U32 | %/s | 1000 | 42017 | 2 | [0.1, 5000]
104 | [Power grid scheduling] Schedule instruction valid duration | RW | U32 | s | 1 | 42019 | 2 | [0, 86400] The value 0 indicates that
the command
is valid permanently.
105 | Failsafe Active Power Limit [kW] [High Accuracy] | RW | I32 | kW | 1000 | 42405 | 2 | [0.000,Pmax]
106 | Time zone | RW | I16 | min | 1 | 43006 | 1 | [–720, 840]
107 | [Management system] TLS encryption | RW | ENUM1 | N/A | N/A | 43098 | 1 | 0: Disabled
|  |  | 6 |  |  |  |  | 1: Enabled
108 | WLAN wakeup | RW | ENUM1 | N/A | N/A | 45052 | 1 | 0: Waken up
|  |  | 6 |  |  |  |  | 1: Disabled
109 | Fast power scheduling | RW | ENUM1 | N/A | N/A | 45086 | 1 | 0: Disable
|  |  | 6 |  |  |  |  | 1: Enable
110 | [Inverter level] Remote charge/discharge control mode | RW | ENUM1 | N/A | N/A | 47589 | 1 | 0: Local control
|  |  | 6 |  |  |  |  | 1: Remote control–Max. self-
consumption
2: Remote control–Fully
fed to grid
3: Remote control–TOU
4: Remote control–AI control 5: Remote Control - Threeparty Scheduling
111 | Scheduled task | RW | ENUM1 | N/A | N/A | 47674 | 1 | 0: Disable
|  |  | 6 |  |  |  |  | 1: Enable
112 | Default maximum feed-in power | RW | INT32 | kW | 1000 | 47675 | 2 | [–1000, plant capacity]
112 | Default active power change gradient | RW | UINT32 | %/s | 1000 | 47677 | 2 | [0.100, 5000.000]
114 | Peak Shaving | RW | ENUM1 | N/A | N/A | 47954 | 1 | 0: Disabled 1: Active power
|  |  | 6 |  |  |  |  | limit 2: Apparent power limit (not supported in the singledevice scenario)
115 | Backup power SOC for peak shaving | RW | UINT16 | % | 10 | 47955 | 1 | [0.0, 100.0]
116 | Peak power | RW | BYTES | N/A | N/A | 47956 | 64
117 | AI optical storage | RW | UINT16 | N/A | N/A | 48020 | 1 | 0: Disabled
1: Enabled
118 | Backup Box model | RW | ENUM1 | N/A | N/A | 48089 | 1 | 0: Backup BoxB0/B1
|  |  | 6 |  |  |  |  | 1: Compatible
Third Party
Backup Box
2: SmartGuard
3: No Backup
Box
119 | Phase-to-ground short-circuit protection | RW | ENUM1 | N/A | N/A | 48090 | 1 | 0: Disabled
|  |  | 6 |  |  |  |  | 1: Enabled
120 | Battery charging mode | RW | ENUM1 | NA | NA | 47086 | 1 | 0: adaptive (fixed charge/ discharge/ maximum selfuse)
|  |  | 6 |  |  |  |  | 1: fixed charge/ discharge 2: maximum
self-use 3: time-of-use electricity price
4: full Internet
access 5:TOU
6: third-party scheduling
121 | Battery charge and discharge power | RW | INT32 | W | 1 | 47321 | 1 | > 0: charging; <
0: discharging; 0: not charging or discharging
122 | [Inverter level] Remote control mode for charging and discharging | RW | ENUM1 | NA | NA | 47589 | 1 | 0: near-end control 1: remote
|  |  | 6 |  |  |  |  | controlmaximum selfuse 2: remote control-full Internet access
3: remote control-Dong
4: remote control - AI energy
management
and scheduling
5: remote control-threeparty scheduling

## sdongle_a_modbus
No. | Signal Name | Read/Write | Data Type | Unit | Gain | Register Address | Quantity | Description
1 | OS Version | RO | STR | N/A | 1 | 30050 | 15 | NA
2 | Protocol Version | RO | U32 | N/A | 1 | 30068 | 2 | High byte : main version. Upgrade it in the case of incompatible versions.
Low byte: release version. Upgrade
it in the case of compatible versions. The baseline version is D5.0. The high byte and low byte are 5 and 0 respectively.
3 | Registration Key | RO | STR | N/A | 1 | 31200 | 10 | NA
4 | SN | RO | STR | N/A | 1 | 30015 | 10 | NA
5 | Type | RO | U16 | N/A | 1 | 37410 | 1 | 0:N/A
2:WLAN
3:4G
5:WLAN-FE
6 | Device Search Status | RO | U16 | N/A | 1 | 37411 | 1 | 0: Search completed
1: Searching
2: Search failed
7 | Device Change Sequence Number | RO | U16 | N/A | 1 | 37412 | 1 | NA
8 | Maximum Number of Devices Allowed | RO | U16 | N/A | 1 | 37429 | 1 | NA
9 | Wireless Route Access Signal Strength | RO | I16 | N/A | 1 | 35104 | 1 | 0X7FFF: Disconnected
0X7FFE:
Disconnected due to authentication failure
[–100, 0]: Signal strength from weak to strong Not supported by
SDongleA-4G
10 | Monthly Used Traffic | RO | U32 | MB | 100 | 35116 | 2 | Supported only by SDongleA-4G
11 | Monthly Remaining Traffic | RO | U32 | MB | 100 | 35118 | 2 | Supported only by SDongleA-4G
12 | Average Daily Used Traffic | RO | U32 | MB | 100 | 35120 | 2 | Supported only by SDongleA-4G
13 | Traffic Status | RO | U16 | N/A | 1 | 35122 | 1 | 0: Normal
1: Warning
2: Used up 0xFF: No package configured
Supported only by
SDongleA-4G
14 | IMEI | RO | STR | N/A | 1 | 35254 | 10 | Supported only by SDongleA-4G
15 | Signal Strength | RO | U16 | N/A | 1 | 35264 | 1 | [0, 5]
0: No signal
Supported only by
SDongleA-4G
16 | System | RO | STR | N/A | 1 | 37430 | 10 | Example: 2G,3G,
4G
Supported only by
SDongleA-4G
17 | Carrier | RO | STR | N/A | 1 | 37440 | 15 | Unknown: Default value or query failed
Supported only by
SDongleA-4G
18 | Total input power | RO | U32 | kw | 100 0 | 37498 | 2 | NA
19 | Load power | RO | U32 | kw | 100 0 | 37500 | 2 | NA
20 | Grid power | RO | INT3 2 | kw | 100 0 | 37502 | 2 | Greater than 0 indicates buy, less
than 0 indicates sell
21 | Total Battery power | RO | INT3 2 | kw | 100 0 | 37504 | 2 | Greater than 0 indicates charge, less than 0 indicates discharge.
22 | Total active power | RO | INT3 2 | kw | 100 0 | 37516 | 2 | NA
23 | Reset | WO | U16 | N/A | 1 | 40205 | 1 | Enter 0 in the data field. After receiving a command, the DSP immediately responds and then resets. After receiving a command, the inverter monitoring module sends it to the DSP. After receiving a normal response, the inverter monitoring module replies to the northbound port and resets after 3s. The system does not
restart if a failure message is replied.
24 | System Time | WO | EPO | N/A | 1 | 40500 | 2 | [2000-01-01
|  |  | CHTI |  |  |  |  | 00:00:00,
|  |  | ME |  |  |  |  | 2068-12-31 23:59:59] Epoch seconds UTC
25 | Daylight Saving Time (DST) | RW | U16 | N/A | 1 | 42900 | 1 | 0: Disabled 1: Enabled Default value:
Disabled
26 | Time Zone | RW | I16 | min | 1 | 43006 | 1 | [–720, 840] Default: 480
(GMT+8 Beijing)
27 | Heartbeat Period at Application Layer | RW | U16 | Min | 1 | 43064 | 1 | [1, 65535]
Default: 30 minutes
28 | TCP Heartbeat Period | RW | U16 | s | 1 | 43065 | 1 | [0, 65535]
Default: 3 minutes
0XFFFF: No heartbeat 0: 3 minutes by default
29 | NMS Server | RW | STR | N/A | 1 | 43067 | 30 | Domain name or IP address
30 | NMS Server Port 1 | RW | U16 | N/A | 1 | 43097 | 1 | [0, 65535]
Default: 27250
31 | SSL Encryption | RW | U16 | N/A | 1 | 43098 | 1 | 0: Disabled
1: Enabled
(default)
32 | NMS Server Port 2 | RW | U16 | N/A | 1 | 43099 | 1 | [0, 65535]
Default: 27251
33 | Port Mode | RW | U16 | N/A | 1 | 43100 | 1 | 0: Dual ports (default)
1: Single port
34 | Registration Status | RW | U16 | N/A | 1 | 43101 | 1 | 0: Unregistered (default)
1: Registered
35 | Unsolicited Report Interval | RW | U16 | Min | 1 | 43134 | 1 | [5, 120]
Default: 5 minutes
0xFFFF:
Unsolicited report not supported If the value is not 5n, round down to the nearest integer multiple of 5.
36 | Reported Data Record Period | RW | U16 | Min | 1 | 43135 | 1 | 5 minutes
(default), 15 minutes, 30 minutes, 60 minutes
37 | NTP Time Synchronization | RW | U16 | N/A | 1 | 43311 | 1 | 0: Disabled (default)
1: Enabled
38 | NTP Server Address | RW | STR | N/A | 1 | 43312 | 30 | NA
39 | NTP Server Port | RW | U16 | N/A | 1 | 43342 | 1 | [0, 65535]
Default: 123
40 | NTP Service Time Synchronization Interval | RW | U16 | min | 1 | 43343 | 1 | [1, 1440]
Default: 5
41 | Card No. | RO | STR | N/A | 1 | 43386 | 10 | ICCID
Supported only by SDongleA-4G
42 | Network Mode | RW | U16 | N/A | 1 | 43430 | 1 | 0 (default):
4G/3G/2G automatic selection 1: 3G/2G automatic selection 2: Only 2G
Supported only by
SDongleA-4G
43 | Traffic Package | RW | U32 | MB | 100 | 43564 | 2 | Supported only by SDongleA-4G
44 | Monthly Used Traffic | RW | U32 | MB | 100 | 43566 | 2 | Used for traffic correction
Supported only by
SDongleA-4G
45 | Connection Port | WO | U16 | N/A | 1 | 45038 | 1 | 1: Port 1
2: Port 2 Other value:
Invalid
46 | Device Operation | WO | STR | N/A | 1 | 47402 | 11 | First 10 registers: Determine the device to be operated based on the SN. Set the register content to the device SN.
Last register:
0: Deletes inverters
1: Reset inverter alarms
47 | Start Device Search | WO | U16 | N/A | 1 | 47413 | 1 | Enter 0 in the data field.

## EMMA
Category | Signal Name | Read/Write | Data Type | Unit | Gain | Register Address | Quantity | Default Value | Range / Description
Characteristic data | Offering name | RO | STR | N/A | N/A | 30000 | 15
Characteristic data | SN | RO | STR | N/A | N/A | 30015 | 10
Characteristic data | Software version | RO | STR | N/A | N/A | 30035 | 15
Characteristic data | Model | RO | STR | N/A | N/A | 30222 | 20
Sampled data | Inverter total absorbed energy | RO | U64 | kWh | 100 | 30302 | 4
Sampled data | Energy charged today | RO | U32 | kWh | 100 | 30306 | 2
Sampled data | Total charged energy | RO | U64 | kWh | 100 | 30308 | 4
Sampled data | Energy discharged today | RO | U32 | kWh | 100 | 30312 | 2
Sampled data | Total discharged energy | RO | U64 | kWh | 100 | 30314 | 4
Sampled data | ESS chargeable energy | RO | U32 | kWh | 1000 | 30318 | 2
Sampled data | ESS dischargeable energy | RO | U32 | kWh | 1000 | 30320 | 2
Sampled data | Rated ESS capacity | RO | U32 | kWh | 1000 | 30322 | 2
Sampled data | Consumption today | RO | U32 | kWh | 100 | 30324 | 2
Sampled data | Total energy consumption | RO | U64 | kWh | 100 | 30326 | 4
Sampled data | Feed-in to grid today | RO | U32 | kWh | 100 | 30330 | 2
Sampled data | Total feed-in to grid | RO | U64 | kWh | 100 | 30332 | 4
Sampled data | Supply from grid today | RO | U32 | kWh | 100 | 30336 | 2
Sampled data | Total supply from grid | RO | U64 | kWh | 100 | 30338 | 4
Sampled data | Inverter energy yield today | RO | U32 | kWh | 100 | 30342 | 2
Sampled data | Inverter total energy yield | RO | U32 | kWh | 100 | 30344 | 2
Sampled data | PV yield today | RO | U32 | kWh | 100 | 30346 | 2
Sampled data | Total PV energy yield | RO | U64 | kWh | 100 | 30348 | 4
Sampled data | PV output power | RO | U32 | kW | 1000 | 30354 | 2
Sampled data | Load power | RO | U32 | kW | 1000 | 30356 | 2
Sampled data | Feed-in power | RO | I32 | kW | 1000 | 30358 | 2
Sampled data | Battery charge/discharge power | RO | I32 | kW | 1000 | 30360 | 2
Sampled data | Inverter rated power | RO | U32 | kW | 1000 | 30362 | 2
Sampled data | Inverter active power | RO | I32 | kW | 1000 | 30364 | 2
Sampled data | SOC | RO | U16 | % | 100 | 30368 | 1
Sampled data | ESS chargeable capacity | RO | U32 | kWh | 1000 | 30369 | 2
Sampled data | ESS dischargeable capacity | RO | U32 | kWh | 1000 | 30371 | 2
Sampled data | Backup power SOC | RO | U16 | % | 100 | 30373 | 1
Sampled data | Yield this month | RO | U32 | kWh | 100 | 30380 | 2
Sampled data | Monthly energy consumption | RO | U32 | kWh | 100 | 30382 | 2
Sampled data | Monthly feed-in to grid | RO | U32 | kWh | 100 | 30384 | 2
Sampled data | Yield this year | RO | U32 | kWh | 100 | 30386 | 2
Sampled data | Annual energy consumption | RO | U32 | kWh | 100 | 30388 | 2
Sampled data | Yearly feed-in to grid | RO | U32 | kWh | 100 | 30390 | 2
Sampled data | Monthly supply from grid | RO | U32 | kWh | 100 | 30394 | 2
Sampled data | Yearly supply from grid | RO | U32 | kWh | 100 | 30396 | 2
SmartGuard | Backup time notification threshold | RO | U16 | min | 1 | 30406 | 1
Sampled data | Energy charged this month | RO | U32 | kWh | 100 | 30407 | 2
Sampled data | Energy discharged this month | RO | U32 | kWh | 100 | 30409 | 2
Device management | Number of inverters found | RO | U16 | N/A | N/A | 30801 | 1
Device management | Number of chargers found | RO | U16 | N/A | N/A | 30804 | 1
Device management | Subdevice presence flag | RO | Bitfield32 | N/A | N/A | 30811 | 2 |  | Bit 0: SmartGuard
Time management | DST state | RO | U16 | N/A | N/A | 31002 | 1 |  | 0: DST not started; 1: DST started
Time management | Local time | RO | U32 | N/A | N/A | 31003 | 2
WiFi management | WiFi-STA signal strength | RO | UINT16 | N/A | N/A | 31135 | 1 |  | [0,4]; 0: no signal
Meter management | Phase A voltage of built-in electric energy sensor | RO | U32 | V | 100 | 31639 | 2
Meter management | Phase B voltage of built-in electric energy sensor | RO | U32 | V | 100 | 31641 | 2
Meter management | Phase C voltage of built-in electric energy sensor | RO | U32 | V | 100 | 31643 | 2
Meter management | A-B line voltage of built-in electric energy sensor | RO | U32 | V | 100 | 31645 | 2
Meter management | B-C line voltage of built-in electric energy sensor | RO | U32 | V | 100 | 31647 | 2
Meter management | C-A line voltage of built-in electric energy sensor | RO | U32 | V | 100 | 31649 | 2
Meter management | Phase A current of built-in electric energy sensor | RO | I32 | A | 10 | 31651 | 2
Meter management | Phase B current of built-in electric energy sensor | RO | I32 | A | 10 | 31653 | 2
Meter management | Phase C current of built-in electric energy sensor | RO | I32 | A | 10 | 31655 | 2
Meter management | Active power of built-in electric energy sensor | RO | I32 | kW | 1000 | 31657 | 2
Meter management | Power factor of built-in electric energy sensor | RO | I32 | N/A | 1000 | 31661 | 2
Meter management | Apparent power of built-in electric energy sensor | RO | I32 | kVA | 1000 | 31663 | 2
Meter management | Phase A active power of built-in electric energy sensor | RO | I32 | kW | 1000 | 31665 | 2
Meter management | Phase B active power of built-in electric energy sensor | RO | I32 | kW | 1000 | 31667 | 2
Meter management | Phase C active power of built-in electric energy sensor | RO | I32 | kW | 1000 | 31669 | 2
Meter management | Total active energy of built-in electric energy sensor | RO | I64 | kWh | 100 | 31671 | 4
Meter management | Total negative active energy of built-in electric energy sensor | RO | I64 | kWh | 100 | 31679 | 4
Meter management | Total positive active energy of built-in electric energy sensor | RO | I64 | kWh | 100 | 31687 | 4
Meter management | Phase A voltage of external electric energy sensor | RO | U32 | V | 10 | 31895 | 2
Meter management | Phase B voltage of external electric energy sensor | RO | U32 | V | 10 | 31897 | 2
Meter management | Phase C voltage of external electric energy sensor | RO | U32 | V | 10 | 31899 | 2
Meter management | A-B line voltage of external electric energy sensor | RO | U32 | V | 10 | 31901 | 2
Meter management | B-C line voltage of external electric energy sensor | RO | U32 | V | 10 | 31903 | 2
Meter management | C-A line voltage of external electric energy sensor | RO | U32 | V | 10 | 31905 | 2
Meter management | Phase A current of external electric energy sensor | RO | I32 | A | 100 | 31907 | 2
Meter management | Phase B current of external electric energy sensor | RO | I32 | A | 100 | 31909 | 2
Meter management | Phase C current of external electric energy sensor | RO | I32 | A | 100 | 31911 | 2
Meter management | Active power of external electric energy sensor | RO | I32 | kW | 1000 | 31913 | 2
Meter management | Power factor of external electric energy sensor | RO | I32 | N/A | 1000 | 31917 | 2
Meter management | Apparent power of external electric energy sensor | RO | I32 | kVA | 1000 | 31919 | 2
Meter management | Phase A active power of external electric energy sensor | RO | I32 | kW | 1000 | 31921 | 2
Meter management | Phase B active power of external electric energy sensor | RO | I32 | kW | 1000 | 31923 | 2
Meter management | Phase C active power of external electric energy sensor | RO | I32 | kW | 1000 | 31925 | 2
Meter management | Total active energy of external electric energy sensor | RO | I64 | kWh | 100 | 31927 | 4
Meter management | Total negative active energy of external electric energy sensor | RO | I64 | kWh | 100 | 31935 | 4
Meter management | Total positive active energy of external electric energy sensor | RO | I64 | kWh | 100 | 31943 | 4
Battery control | ESS control mode | RW | ENUM16 | N/A | N/A | 40000 | 1 | 2 | 1: reserved; 2: maximum self-consumption; 3: reserved; 4: fully fed to grid; 5: time of use; 6: third-party dispatch
Battery control | [Time of Use mode] Preferred use of surplus PV power | RW | ENUM16 | N/A | N/A | 40001 | 1 | 1 charge | 0: fed to grid 1 charge
Battery control | [Time of Use mode] Maximum power for charging batteries from grid | RW | U32 | kW | 1000 | 40002 | 2 |  | [0, 50.000]
Battery control | [Time of Use mode] Charge / Discharge time window | RW | MLD | N/A | N/A | 40004 | 43
Limited feed-in | Power control mode at grid connection point | RW | ENUM16 | N/A | N/A | 40100 | 1 | 0 | 0: unlimited; 5: grid connected with zero power; 6: limited feed-in (kW); 7: power-limited grid connected (%)
Limited feed-in | Limitation mode | RW | ENUM16 | NA | NA | 40101 | 1 | 0: total power | 0: total power 1 single-phase power
Limited feed-in | Maximum grid feed-in power (kW) | RW | I32 | kW | 1000 | 40107 | 2 | 0 | [–1, Pmax]
Limited feed-in | Maximum grid feed-in power (%) | RW | U16 | % | 10 | 40109 | 1 | 0 | [0, 100.0]
Limited feed-in | Three-phase imbalance control | RW | ENUM16 | N/A | N/A | 40110 | 1 | 0 | 0: disabled; 1: enabled
Time management | System time | RW | U32 | N/A | 1 | 40470 | 2
Time management | Local time year | RW | U16 | N/A | 1 | 40490 | 1 |  | [2000,2068]
Time management | Local time - month | RW | U16 | N/A | 1 | 40491 | 1 |  | [1,12]
Time management | Local time - day | RW | U16 | N/A | 1 | 40492 | 1 |  | [1,31]
Time management | Local time hour | RW | U16 | N/A | 1 | 40493 | 1 |  | [0,23]
Time management | Local time - minute | RW | U16 | N/A | 1 | 40494 | 1 |  | [0,59]
Time management | Local time - second | RW | U16 | N/A | 1 | 40495 | 1 |  | [0,59]
SmartGuard | Power supply configuration | RW | ENUM16 | N/A | N/A | 41214 | 1 | 0 | 0: none 1 mains only 2 mains + generator 3 generator only
SmartGuard | Consider mains to be faulty if | RW | ENUM16 | N/A | N/A | 41215 | 1 | 0 | 0: open; 1: closed

## EMMA Smart Meter
Signal Name | Status | Read/Write | Data Type | Unit | Gain | Register Address | Quantity | Default Value | Range / Description
Running status | Valid | RO | ENU M16 | N/A | N/A | 30500 | 1 |  | 0: online
0.041667
offline
Phase A voltage | Valid | RO | U32 | V | 100 | 30502 | 2
Phase B voltage | Valid | RO | U32 | V | 100 | 30504 | 2
Phase C voltage | Valid | RO | U32 | V | 100 | 30506 | 2
A-B line voltage | Valid | RO | U32 | V | 100 | 30508 | 2
B-C line voltage | Valid | RO | U32 | V | 100 | 30510 | 2
C-A line voltage | Valid | RO | U32 | V | 100 | 30512 | 2
Phase A current | Valid | RO | I32 | A | 10 | 30514 | 2
Phase B current | Valid | RO | I32 | A | 10 | 30516 | 2
Phase C current | Valid | RO | I32 | A | 10 | 30518 | 2
Active power | Valid | RO | I32 | kW | 1000 | 30520 | 2
Power | Valid | RO | I32 | N/A | 1000 | 30524 | 2
factor
Apparent power | Valid | RO | I32 | kVA | 1000 | 30526 | 2
Phase A active | Valid | RO | I32 | kW | 1000 | 30528 | 2
power
Phase B active | Valid | RO | I32 | kW | 1000 | 30530 | 2
power
Phase C active | Valid | RO | I32 | kW | 1000 | 30532 | 2
power
Total active energy | Valid | RO | I64 | kWh | 100 | 30534 | 4
Total negative active energy | Valid | RO | I64 | kWh | 100 | 30542 | 4
Total positive active energy | Valid | RO | I64 | kWh | 100 | 30550 | 4

## smartcharger_emma_modbus
Signal Name | Status | Read/Write | Data Type | Unit | Gain | Register Address | Quantity | Default Value | Range / Description
Offering name | Valid | RO | STR | NA | NA | 30000 | 15
ESN | Valid | RO | STR | NA | NA | 30015 | 16
Software version | Valid | RO | STR | NA | NA | 30031 | 16
Rated power | Valid | RO | U32 | kW | 10 | 30076 | 2 |  | [0,100]
Charger model | Valid | RO | STR | NA | NA | 30078 | 14
Bluetooth name | Valid | RO | STR | NA | NA | 30094 | 16
Phase A voltage | Valid | RO | U32 | V | 10 | 30500 | 2 |  | [0,800]
Phase B voltage | Valid | RO | U32 | V | 10 | 30502 | 2 |  | [0,800]
Phase C voltage | Valid | RO | U32 | V | 10 | 30504 | 2 |  | [0,800]
Total energy charged | Valid | RO | U32 | kWh | 1000 | 30506 | 2
Charger temperature | Valid | RO | I32 | °C | 10 | 30508 | 2 |  | [–100,+200]

## EMMA SUN2000
Signal Name | Read/Write | Data Type | Register Address | Quantity | Description
Active alarm | RO | U32 | 65500 | 2 | Specifies the sequence number of an active alarm of the device; used for alarm synchronization on the management system.
SN
Histori cal alarm | RO | U32 | 65502 | 2 | Specifies the sequence number of a historical alarm of the device; used for alarm synchronization on the management system.
SN
Device SN | RO | STR | 65510 | 10 | A unified top-level interface is provided for querying device ESNs.
-- For a Huawei-developed device (such as inverter) that has an ESN, the EMMA reads the ESN of the inverter and copies it to the common register.
-- For a third-party device (such as Shelly circuit breaker), that does not have an ESN, the EMMA automatically generates an ESN for the device.
Device alias | RW | STR | 65524 | 10 | Specifies the device name to be displayed to the user.
-- The model information on the nameplates of the SmartGuard, EMMA, and inverter as the default values for these devices.
-- The default value is My Charging Pile for a charger.
Device connec tion status | RO | U16 | 65534 | 1 | A unified interface for device status query is provided to query the online and offline status of devices.